[image: image1.jpg]





In these conditions,
‘Council’ means: the Corporation of the City of Marion, 
‘Owner’ means: the persons holding the title of the property on which the service is to be connected.
‘Builder’ means: the person / company in charge of building the property.
‘Contractor’ means party or parties performing the laying of the service at the request of the owner / builder.
‘Applicant’ means: the party applying for the work to proceed on behalf of the owner / builder or contractor.

The issuing of this authorisation is subject to the applicant advising the owner, builder, contractor with all parties reaching agreement to the conditions of authorisation as detailed below.
The company undertaking this work must have a current public liability insurance with a minimum cover of $20 million.  Without current public liability insurance this authorisation is invalid. 
CONDITIONS:

1. Prior to works, the contractors shall undertake all necessary Dial Before You Dig and service location enquiries and contact any relevant authorities necessary. 
2. The electrical service shall be laid at a minimum depth of 600mm below the present or proposed surface, whichever be the lower.

3. Where the pole is located either on the alignment of the property boundary or in front of the property, the underground electrical service is to be at 900 to the property line. Where it is impracticable for the underground electrical service to enter the property directly opposite the pole from which it originates, a square route from the pole along the footpath at a maximum of 300mm out from the property line and across to the property at 900 to the property line, shall be followed.  The underground electrical service shall access the property at a point nearest the pole.

4. All wiring is to be enclosed in orange conduit, have electrical warning tape fitted 300mm above the pipe and laid in accordance with the Australian Standard Specifications AS/NZS 3000:2018 (SAA Wiring Rules) and AS 2053 (Non-metallic Conduit and Fittings).
5. The contractor will be permitted to excavate and remove sections of Council footpath, roadway and verge to facilitate placement of the underground electrical service.  
6. Any works around the tree protection zones particularly near regulated trees must be completed using a hydra vac with Council’s arborist being informed prior to intended works via email to council@marion.sa.gov.au.

7. The contractor shall ensure the works is in accordance with all industry work and safety standards and relevant codes of practice, this includes keeping the site safe during the works by erecting appropriate signs, barricades and ensuring the area free of any hazards.
8. The contractor must ensure that the works do not interfere with or cause damage to or in any way affect the property of any other person.
9. Reinstatement of Council assets related to the electrical service installation shall be arranged by the contractor on behalf of the builder and owner.  The work will not be deemed complete until such time that the trench and any damage caused is appropriately back filled, and all surfaces are reinstated in matching material. 
10. All reinstatement works must be properly compacted, conform to council standards and finished to a high-quality meeting the satisfaction of Councils Civil Services.
- All trenches under footpath is to be compacted to Council standard SD-21-Footpath
- All trenches within Council’s verge is to be compacted to meet Council standard SD-22-Reserve
- All trenches under Council’s road is to be compacted to meet Council standard SD-20-Road
11. All damaged sections of concrete must be reinstated to the full width of the footpath and joint to joint.   Longitudinal trenches through concrete footpaths are not permitted by council. All asphalt reinstatements are to be cut square and joined using an adhesion/bonding agent.
12. Should the trench not be completed to council standards within a suitable timeframe as decided by Council or the area is left unsafe, Council retains the right without explanation to complete any rectification works and invoice the owner, builder, or contractor accordingly.  
13. The electrical service installation shall be certified by the electrical contractor in accordance with the relevant Australian Standard Specifications.

14. Any future alterations necessary to this installation through road widening or other works shall be carried out by the owner at no cost to the Council.
15. No work shall be performed on site prior to Council approval of the application form.
16. The Council, its servants or agents accept no responsibility and are indemnified from any cost, claims, demands for injury, loss, or damage in relation to the works approved in this application.

17. The applicant shall make the contractor, owner, and builder aware that they shall be liable for any costs, claims, demands for injury, loss or damage in relation to the works approved in this application.
PLAN REQUIREMENTS
A plan is to be drawn in a neat and legible manner and attached to the application, showing:
a) Location of the property, property boundaries in relation to street alignment.

b) Position of electricity pole in relation to allotment and roadway.
c) Precise location and measurements of proposed trench.
d) All known services inspection points, service pits and trees.
e) Location of service inside property.
CONTACT DETAILS



T (08) 8375 6600

F (08) 8375 6699

E council@marion.sa.gov.au

PO Box 21 
Park Holme South Australia 5043

www.marion.sa.gov.au
Underground Electrical Service


Conditions 









marion.sa.gov.au ( Underground Electrical Service Application Conditions
Page 2 of 2

